FIRE ALARM INSTALLATION REQUIREMENTS

Fire alarm / detection systems shall be installed with an approved fire alarm

permit and in accordance with NFPA 72, International Fire Code,

International Building Code and the requirements listed below:

General Information:

- All systems shall be installed according to the International Fire Code, International Building Code and the National Fire Protection Association (NFPA) 72.

- All system components must be listed by Underwriters Laboratory (UL) and installed in accordance with their listing.

- All newly installed fire alarm systems shall be addressable with point identification.  The identification (panel read out wording shall be approved by the Bensalem Fire Rescue Dept).

    - Each initiating deceive shall be labeled to coincide with the FACP and the annunciator panel.

    - Zoned systems are permitted if approved by Bensalem Fire Rescue Dept , but each initiating device shall have its own zone (example: Zone #1 Front Pull Station, Zone #2 Smoke Detector Electrical Room, Zone # 3 Water flow Alarm).

- A copy of the approved plan and permit shall be on site at all times.

- A Knox Box shall be installed at an approved location 6’ off grade.

- A weather proofed horn/strobe shall be installed above the Knox Box, 10’ off of grade.

- The fire alarm control panel or a remote annunciator panel shall be located at the main entrance or at a location approved by the Bensalem Fire Rescue Dept.

- Duct Detectors, elevator recall, low air pressure and low temperature switches shall be monitored for supervision only.

- Remote test switches are required for all duct detectors.

- All suppression systems (sprinkler, cooking hood suppression systems, FM 200 systems and all other alternative extinguishing systems) shall be interconnected with the buildings fire alarm system.

- Water flow alarms shall report as a Water flow alarm not a general fire alarm.

- An NFPA 72 installation and record of completion form is required at the time of the final inspection.