FIRE ALARM TESTING / CERTIFICATION REQUIREMENTS

Fire alarm / detection systems shall be tested/ certified in accordance with NFPA 72, International Fire Code, International Building Code and the requirements listed below:

Testing Information (Certification Test):

- Bensalem Fire Rescue shall be on site to witness the Fire Alarm Function Test.

    - Contact the Bensalem Township Building & Plan Dept. to schedule a Fire Alarm and 24 hr Battery Test.

    - Fire Alarm Function Tests are only scheduled Monday – Thursday.

    - Battery Tests are only scheduled Tuesday – Friday.

    - If you need a test during after hours or on weekends it must be approved by the Bensalem Fire Rescue Dept and an overtime fee will be charged.

- A copy of the approved plans and permit shall be on-site at all times.

- All devices will be tested for proper operation. Smoke detectors, heat detectors, pull stations, water flow switches, duct detectors, etc.

- All sprinkler control valves shall be tested. (The fire pump will also be tested if present).

- Confirm the Bensalem Fire Rescue approved addressable locations / point identifications for each device.

- All horns and strobes will be tested. The decibel level and light intensity shall be set correctly and synchronized.

- A key for the building, a manual pull station key, a FACP key and the code for the fire alarm shall be locked in the Knox Box.

- The primary and secondary phone lines will be tested.

- All magnetic door devices release, doors close and latch on activation of any device will be tested.

- All ventilation systems shall shutdown upon activation of duct smoke detectors.

- All smoke / fire dampers shall close upon activation. The dampers do not have to be interconnected.

- Contact the alarm monitoring company and Bucks County Fire Radio / Dispatch Center (215-547-5222) to verify that the correct signals and addresses were received.

- 24-Hour Battery Test is required; the AC power will be secured for the battery test.  (Bensalem Fire Rescue will be on site for the battery test).

- Completed copy of the NFPA 72 Record of Completion Form is required at the completion of the 24 hours battery test.  Bensalem Fire Rescue shall receive a copy at the completion of the Certification Test.